## Objects
Object Name | Data Type | Units | Object Number | Property Identifier | Description | Valid Input Values | Default Value | Writeable: N, Y, R, U
Object Type Device (Object_Type = 8)
Device | ObjectId |  | Serial# | Object_Identifier (75) | Network-wide unique identifier. Defaults to serial number | Any 22 bit unsigned integer | Device, Serial# | Y
Device | String |  | Serial# | Object_Name (77) | Network-wide unique name. Defaults to model and serial number | Any character string | Model, Serial# | N
Device | BACnetObjectType |  | Serial# | Object_Type (79) | 8 = Device Object Type | none | 8 | N
Device | BACnetDeviceStatus |  | Serial# | System_Status (112) | 0 = operational 1 = operational-read-only 2 = download-required 3 = download-in-progress 4 = non-operational 5 = backup-in-progress | none | 0 | N
Device | String |  | Serial# | Vendor_Name (121) | Manufacturer | none | Continental Control Systems, LLC | N
Device | UInt16 |  | Serial# | Vendor_Identifier (120) | Unique ID assigned by ASHRAE | none | 500 | N
Device | String |  | Serial# | Model_Name (70) | The product model number | none |  | N
Device | String |  | Serial# | Firmware_Revision (44) | The product firmware version | none | 1.04 | N
Device | String |  | Serial# | Application_Software_Version (12) | The product application version (same as firmware version) | none | 1.04 | N
Device | String |  | Serial# | Location (58) | User configurable (30 characters) | none | Unspecified | Y
Device | String |  | Serial# | Description (28) | User configurable (30 characters) | none | AC Power and Energy Meter | Y
Device | Unsigned |  | Serial# | Protocol_Version (98) | BACnet protocol version | none | 1 | N
Device | Unsigned |  | Serial# | Protocol_Revision (139) | BACnet protocol revision | none | 10 | N
Device | BACnetServicesSupported |  | Serial# | Protocol_Services_Supported (97) | List of all the BACnet services supported | none | AtomicWriteFile, ReadProperty, ReadPropertyMultiple, WriteProperty, WritePropertyMultiple, ReinitializeDevice, IAm, IHave | N
Device | BACnetObjectTypesSupported |  | Serial# | Protocol_Object_Types_Supported (96) | List of all supported BACnet object types | none | Analog Input, Analog Value, Binary Value, Device, Multi-state Value, File Object | N
Device | BACnetARRAY[N] of ObjectId |  | Serial# | Object_List (76) | List of all the objects | none |  | N
Device | Unsigned |  | Serial# | Max_APDU_Length_Accepted (62) |  | none | 480 | N
Device | BACnetSegmentation |  | Serial# | Segmentation_Supported (107) | 3 = "no segmentation" | none | 3 | N
Device | Unsigned | milliseconds | Serial# | APDU_Timeout (11) | Application request timeout | none | 0 | N
Device | Unsigned |  | Serial# | Number_Of_APDU_Retries (73) |  | none | 3 | N
Device | List of BACnetAddressBinding |  | Serial# | Device_Address_Binding (30) |  | none |  | N
Device | UInt8 |  | Serial# | Max_Master (64) | Highest possible address for master nodes | 1 to 127 | 127 | Y
Device | Unsigned |  | Serial# | Max_Info_Frames (63) | Max number of information frames the node may send before it must pass the token | 1 to 255 | 1 | Y
Device | Unsigned |  | Serial# | Database_Revision (155) |  | none | 0 | N
Object Type Analog Input (Object_Type = 0)
EnergySumNR | Float | Kilowatt Hours | 0 | Present_Value (85) | Total net energy, non-resettable | none |  | N
EnergySumNRInt | Int32 | 0.1 Kilowatt Hours | 0 | Integer_Value (1000) | Total net energy, non-resettable | none |  | N
EnergyPosSumNR | Float | Kilowatt Hours | 1 | Present_Value (85) | Total positive energy, non-resettable | none |  | N
EnergyPosSumNRInt | Int32 | 0.1 Kilowatt Hours | 1 | Integer_Value (1000) | Total positive energy, non-resettable | none |  | N
EnergyNegSumNR | Float | Kilowatt Hours | 2 | Present_Value (85) | Total negative energy | none |  | N
EnergyNegSumNRInt | Int32 | 0.1 Kilowatt Hours | 2 | Integer_Value (1000) | Total negative energy | none |  | N
PowerSum | Float | Watts | 3 | Present_Value (85) | Total power | none |  | N
PowerA | Float | Watts | 4 | Present_Value (85) | Power for phase A (watts) | none |  | N
PowerB | Float | Watts | 5 | Present_Value (85) | Power for phase B (watts) | none |  | N
PowerC | Float | Watts | 6 | Present_Value (85) | Power for phase C (watts) | none |  | N
PowerReacSum | Float | Volt Amperes Reactive | 7 | Present_Value (85) | Reactive power sum | none |  | N
PowerReacA | Float | Volt Amperes Reactive | 8 | Present_Value (85) | Per-phase reactive energy phase A | none |  | N
PowerReacB | Float | Volt Amperes Reactive | 9 | Present_Value (85) | Per-phase reactive energy phase B | none |  | N
PowerReacC | Float | Volt Amperes Reactive | 10 | Present_Value (85) | Per-phase reactive energy phase C | none |  | N
PowerAppSum | Float | Volt Amperes | 11 | Present_Value (85) | Apparent power sum | none |  | N
PowerAppA | Float | Volt Amperes | 12 | Present_Value (85) | Apparent power for phase A | none |  | N
PowerAppB | Float | Volt Amperes | 13 | Present_Value (85) | Apparent power for phase B | none |  | N
PowerAppC | Float | Volt Amperes | 14 | Present_Value (85) | Apparent power for phase C | none |  | N
VoltAvgLN | Float | Volts | 15 | Present_Value (85) | Average RMS L-N voltage active phases | none |  | N
VoltA | Float | Volts | 16 | Present_Value (85) | RMS voltage L-N phase A | none |  | N
VoltB | Float | Volts | 17 | Present_Value (85) | RMS voltage L-N phase B | none |  | N
VoltC | Float | Volts | 18 | Present_Value (85) | RMS voltage L-N phase C | none |  | N
VoltAvgLL | Float | Volts | 19 | Present_Value (85) | Average RMS L-L voltage for active phases | none |  | N
VoltAB | Float | Volts | 20 | Present_Value (85) | RMS voltage L-L phase A-B | none |  | N
VoltBC | Float | Volts | 21 | Present_Value (85) | RMS voltage L-L phase B-C | none |  | N
VoltAC | Float | Volts | 22 | Present_Value (85) | RMS voltage L-L phase A-C | none |  | N
Freq | Float | Hertz | 23 | Present_Value (85) | Line frequency (Hz) | none |  | N
CurrentA | Float | Amperes | 24 | Present_Value (85) | RMS current for phase A | none |  | N
CurrentB | Float | Amperes | 25 | Present_Value (85) | RMS current for phase B | none |  | N
CurrentC | Float | Amperes | 26 | Present_Value (85) | RMS current for phase C | none |  | N
PowerFactorAvg | Float | No Units | 27 | Present_Value (85) | Average power factor for all phases | none |  | N
PowerFactorA | Float | No Units | 28 | Present_Value (85) | Power factor for phase A | none |  | N
PowerFactorB | Float | No Units | 29 | Present_Value (85) | Power factor for phase B | none |  | N
PowerFactorC | Float | No Units | 30 | Present_Value (85) | Power factor for phase C | none |  | N
Demand | Float | Watts | 31 | Present_Value (85) | Real power demand averaged over 1 minute to 12 hours | none |  | U, R
DemandApp | Float | Watts | 32 | Present_Value (85) | Apparent power demand averaged over 1 minute to 12 hours | none |  | U, R
DemandA | Float | Watts | 33 | Present_Value (85) | Phase A real power demand averaged over 1 minute to 12 hours | none |  | U, R
DemandB | Float | Watts | 34 | Present_Value (85) | Phase B real power demand averaged over 1 minute to 12 hours | none |  | U, R
DemandC | Float | Watts | 35 | Present_Value (85) | Phase C real power demand averaged over 1 minute to 12 hours | none |  | U, R
DemandMin | Float | Watts | 36 | Present_Value (85) | Minimum demand since reset | none |  | U, R
DemandMax | Float | Watts | 37 | Present_Value (85) | Maximum demand since reset | none |  | U, R
EnergySum | Float | Kilowatt Hours | 38 | Present_Value (85) | Total net energy (kWh), resettable | ±100GWh |  | U, R
EnergySumInt | Int32 | 0.1 Kilowatt Hours | 38 | Integer_Value (1000) | Total net energy (kWh), resettable | ±100GWh |  | U, R
EnergyPosSum | Float | Kilowatt Hours | 39 | Present_Value (85) | Total positive energy (kWh), resettable | 0 to +100GWh |  | U, R
EnergyPosSumInt | Int32 | 0.1 Kilowatt Hours | 39 | Integer_Value (1000) | Total positive energy (kWh), resettable | 0 to +100GWh |  | U, R
EnergyNegSum | Float | Kilowatt Hours | 40 | Present_Value (85) | Total negative energy | 0 to +100GWh |  | U, R
EnergyNegSumInt | Int32 | 0.1 Kilowatt Hours | 40 | Integer_Value (1000) | Total negative energy | 0 to +100GWh |  | U, R
EnergyA | Float | Kilowatt Hours | 41 | Present_Value (85) | Per-phase energy | ±100GWh |  | U, R
EnergyAInt | Int32 | 0.1 Kilowatt Hours | 41 | Integer_Value (1000) | Per-phase energy | ±100GWh |  | U, R
EnergyB | Float | Kilowatt Hours | 42 | Present_Value (85) | Per-phase energy | ±100GWh |  | U, R
EnergyBInt | Int32 | 0.1 Kilowatt Hours | 42 | Integer_Value (1000) | Per-phase energy | ±100GWh |  | U, R
EnergyC | Float | Kilowatt Hours | 43 | Present_Value (85) | Per-phase energy | ±100GWh |  | U, R
EnergyCInt | Int32 | 0.1 Kilowatt Hours | 43 | Integer_Value (1000) | Per-phase energy | ±100GWh |  | U, R
EnergyPosA | Float | Kilowatt Hours | 44 | Present_Value (85) | Per-phase positive energy phase A | 0 to +100GWh |  | U, R
EnergyPosAInt | Int32 | 0.1 Kilowatt Hours | 44 | Integer_Value (1000) | Per-phase positive energy phase A | 0 to +100GWh |  | U, R
EnergyPosB | Float | Kilowatt Hours | 45 | Present_Value (85) | Per-phase positive energy phase B | 0 to +100GWh |  | U, R
EnergyPosBInt | Int32 | 0.1 Kilowatt Hours | 45 | Integer_Value (1000) | Per-phase positive energy phase B | 0 to +100GWh |  | U, R
EnergyPosC | Float | Kilowatt Hours | 46 | Present_Value (85) | Per-phase positive energy phase C | 0 to +100GWh |  | U, R
EnergyPosCInt | Int32 | 0.1 Kilowatt Hours | 46 | Integer_Value (1000) | Per-phase positive energy phase C | 0 to +100GWh |  | U, R
EnergyNegA | Float | Kilowatt Hours | 47 | Present_Value (85) | Per-phase negative energy phase A | 0 to +100GWh |  | U, R
EnergyNegAInt | Int32 | 0.1 Kilowatt Hours | 47 | Integer_Value (1000) | Per-phase negative energy phase A | 0 to +100GWh |  | U, R
EnergyNegB | Float | Kilowatt Hours | 48 | Present_Value (85) | Per-phase negative energy phase B | 0 to +100GWh |  | U, R
EnergyNegBInt | Int32 | 0.1 Kilowatt Hours | 48 | Integer_Value (1000) | Per-phase negative energy phase B | 0 to +100GWh |  | U, R
EnergyNegC | Float | Kilowatt Hours | 49 | Present_Value (85) | Per-phase negative energy phase C | 0 to +100GWh |  | U, R
EnergyNegCInt | Int32 | 0.1 Kilowatt Hours | 49 | Integer_Value (1000) | Per-phase negative energy phase C | 0 to +100GWh |  | U, R
EnergyReacSum | Float | kVARh | 50 | Present_Value (85) | Net reactive energy sum | ±100GWh |  | U, R
EnergyReacSumInt | Int32 | 0.1 kVARh | 50 | Integer_Value (1000) | Net reactive energy sum | ±100GWh |  | U, R
EnergyReacA | Float | kVARh | 51 | Present_Value (85) | Per-phase reactive energy phase A | ±100GWh |  | U, R
EnergyReacAInt | Int32 | 0.1 kVARh | 51 | Integer_Value (1000) | Per-phase reactive energy phase A | ±100GWh |  | U, R
EnergyReacB | Float | kVARh | 52 | Present_Value (85) | Per-phase reactive energy phase B | ±100GWh |  | U, R
EnergyReacBInt | Int32 | 0.1 kVARh | 52 | Integer_Value (1000) | Per-phase reactive energy phase B | ±100GWh |  | U, R
EnergyReacC | Float | kVARh | 53 | Present_Value (85) | Per-phase reactive energy phase C | ±100GWh |  | U, R
EnergyReacCInt | Int32 | 0.1 kVARh | 53 | Integer_Value (1000) | Per-phase reactive energy phase C | ±100GWh |  | U, R
EnergyAppSum | Float | kVAh | 54 | Present_Value (85) | Apparent energy sum | 0 to +100GWh |  | U, R
EnergyAppSumInt | Int32 | 0.1 kVAh | 54 | Integer_Value (1000) | Apparent energy sum | 0 to +100GWh |  | U, R
EnergyAppA | Float | kVAh | 55 | Present_Value (85) | Per-phase apparent energy phase A | 0 to +100GWh |  | U, R
EnergyAppAInt | Int32 | 0.1 kVAh | 55 | Integer_Value (1000) | Per-phase apparent energy phase A | 0 to +100GWh |  | U, R
EnergyAppB | Float | kVAh | 56 | Present_Value (85) | Per-phase apparent energy phase B | 0 to +100GWh |  | U, R
EnergyAppBInt | Int32 | 0.1 kVAh | 56 | Integer_Value (1000) | Per-phase apparent energy phase B | 0 to +100GWh |  | U, R
EnergyAppC | Float | kVAh | 57 | Present_Value (85) | Per-phase apparent energy phase C | 0 to +100GWh |  | U, R
EnergyAppCInt | Int32 | 0.1 kVAh | 57 | Integer_Value (1000) | Per-phase apparent energy phase C | 0 to +100GWh |  | U, R
Object Type Analog Value (Object_Type = 2)
ErrorStatus1 | Float | No Units | 0 | Present_Value (85) | Most recent error code | none | 0 | N
ErrorStatus2 | Float | No Units | 1 | Present_Value (85) | 2nd most recent error code | none | 0 | N
ErrorStatus3 | Float | No Units | 2 | Present_Value (85) | 3rd most recent error code | none | 0 | N
ErrorStatus4 | Float | No Units | 3 | Present_Value (85) | 4th most recent error code | none | 0 | N
ErrorStatus5 | Float | No Units | 4 | Present_Value (85) | 5th most recent error code | none | 0 | N
ErrorStatus6 | Float | No Units | 5 | Present_Value (85) | 6th most recent error code | none | 0 | N
ErrorStatus7 | Float | No Units | 6 | Present_Value (85) | 7th most recent error code | none | 0 | N
ErrorStatus8 | Float | No Units | 7 | Present_Value (85) | 8th most recent error code | none | 0 | N
UptimeSecs | Float | Seconds | 8 | Present_Value (85) | Runtime since last power cycle | none | 0 | N
TotalSecs | Float | Seconds | 9 | Present_Value (85) | Total accumulated runtime | none | 0 | N
PowerCycles | Float | No Units | 10 | Present_Value (85) | Total accumulated power cycles | none | 1 | N
ConfigPasscode | Float | No Units | 11 | Present_Value (85) | Used to unlock access to user password protected registers | any | 0 | U
CtAmpsA | Float | Amperes | 12 | Present_Value (85) | CT Amps for phase A | 0 to 60000 | 5 | U
CtAmpsB | Float | Amperes | 13 | Present_Value (85) | CT Amps for phase B | 0 to 60000 | 5 | U
CtAmpsC | Float | Amperes | 14 | Present_Value (85) | CT Amps for phase C | 0 to 60000 | 5 | U
DemPerMins | Float | Minutes | 15 | Present_Value (85) | Demand period | 1 to 720 | 15 | U
DemSubints | Float | No Units | 16 | Present_Value (85) | Number of demand subintervals | 1 to 10 | 1 | U
GainAdjustA | Float | No Units | 17 | Present_Value (85) | Optionally adjust the power/energy gain (calibration) for phase A | 5000 to 20000 | 10000 | U
GainAdjustB | Float | No Units | 18 | Present_Value (85) | Optionally adjust the power/energy gain (calibration) for phase B | 5000 to 20000 | 10000 | U
GainAdjustC | Float | No Units | 19 | Present_Value (85) | Optionally adjust the power/energy gain (calibration) for phase C | 5000 to 20000 | 10000 | U
PhaseAdjustA | Float | Degrees Angular | 20 | Present_Value (85) | Phase A adjustment values. Used to compensate CTs (millidegrees) | -8000 to +8000 | -1000 | U
PhaseAdjustB | Float | Degrees Angular | 21 | Present_Value (85) | Phase B adjustment values. Used to compensate CTs (millidegrees) | -8000 to +8000 | -1000 | U
PhaseAdjustC | Float | Degrees Angular | 22 | Present_Value (85) | Phase C adjustment values. Used to compensate CTs (millidegrees) | -8000 to +8000 | -1000 | U
CreepLimit | Float | No Units | 23 | Present_Value (85) | Minimum power for a non-zero power reading | 100 to 10000 | 1500 | U
PtRatio | Float | No Units | 24 | Present_Value (85) | Voltage Transformer Ratio used in medium voltage applications | 0.05 to 300.0 | 1 | U
CalPasscode | Float | No Units | 25 | Present_Value (85) | Used to unlock write access to calibration registers | any |  | Y
Object Type Binary Value (Object_Type = 5)
InvertCtA | Boolean | No Units | 0 | Present_Value (85) | Per-phase software compensation for A phase CT orientation | ACTIVE, INACTIVE | INACTIVE | U
InvertCtB | Boolean | No Units | 1 | Present_Value (85) | Per-phase software compensation for B phase CT orientation. | ACTIVE, INACTIVE | INACTIVE | U
InvertCtC | Boolean | No Units | 2 | Present_Value (85) | Per-phase software compensation for C phase CT orientation | ACTIVE, INACTIVE | INACTIVE | U
ClearErrors | Boolean | No Units | 3 | Present_Value (85) | Clears the ErrorStatus queue | ACTIVE, INACTIVE | INACTIVE | Y
ZeroEnergy | Boolean | No Units | 4 | Present_Value (85) | Resets the energy registers | ACTIVE, INACTIVE | INACTIVE | U
RecallDefaults | Boolean | No Units | 5 | Present_Value (85) | Recalls the factory default setup | ACTIVE, INACTIVE | INACTIVE | U
Wink | Boolean | No Units | 6 | Present_Value (85) | Display cycling LED pattern | ACTIVE, INACTIVE | INACTIVE | U
Object Type Multi-State Value (Object_Type = 19)
BaudRate | Enumerated | No Units | 0 | Present_Value (85) | Read the current baud rate | 0 = 9,600 Baud 1 = 19,200 Baud 2 = 38,400 Baud 3 = 57,600 Baud 4 = 76,800 Baud | N/A | N
PasscodeEnabled | Enumerated | No Units | 1 | Present_Value (85) | Reads the state of user configuration access | 0 = No Passcode 1 = Locked 2 = Unlocked | 0 = No Passcode | N
PhaseOffset | Enumerated | No Units | 2 | Present_Value (85) | Circuit type used to compute line-to-line voltages | 0 = Single-Phase 1 = 3Ø Grounded Delta 2 = 3Ø High-Leg Delta 3 = 3Ø Balanced 4 = 1Ø Center Neutral | 3 = Three Phase Balanced | U
Averaging | Enumerated | No Units | 3 | Present_Value (85) | Measurement averaging modes | 0 = Fastest (1 sec.) 1 = Fast (5 sec.) 2 = Medium (20 sec.) 3 = Slow (60 sec.) | 1 = Fast | U
ZeroDemand | Unsigned | No Units | 4 | Present_Value (85) | Restart or reset demand measurements | 0 = No Change 1 = Reset Min Max 2 =Start New Inteval 3 = Reset and Start | 0 = No Change | U
Note on I1: Indicates if this register can be written: N = No Y = Yes R = May be reset to zero U = User passcode protectable