## Instructions
SunSpec PICS Template
This SunSpec PICS template was generated by SunSpec Dashboard v1.0.6 based on the model contents of the connected device.
Most of the necessary information is populated but the PICS must be completed before submission by performing the following steps:
1. Examine the entry in the 'Value' column for each point to verify correctness:
- Common model (1) points that are implemented should contain the current value.
- All other model points that are implemented and have a variable value should contain the string 'supported'.
- All other model points that are implemented and have a constant value should contain the constant value.
It is assumed that scale factors are constants. If they are not, change the value to 'supported'.
- All unimplemented points should contain the string 'unimplemented'.
- For each enumeration or bit field entry that is not implemented, change the string to 'unimplemented'.
2. Examine the 'R/W' column to ensure the access is correct. It should be either 'R' or 'RW'.
3. For any point that has an implementation deviation or special considerations indicate the issue in the 'Conformance Notes' column.
The certificate number will be filled in when certification is complete and this file will be archived with the Testing Info tab removed
along with a copy of the certificate on sunspec.org.

## Certification Info
Certificate Number | 034-001
Date | 2018-12-03
Manufacturer Name | Continental Control Systems
Product Name | WattNode Modbus
Product Models | WND-WR-MB, WND-M1-MB, WND-xx-xxx-MB
Product Description | 3-Phase Power/Energy Meter

## Testing Info
Submitter | Nick Jancewicz
Email | nick.jancewicz@ctlsys.com
Phone | (720) 287-8424
Interface Type | TCP/RTU
Baud Rate | 19200
Slave Id | 1

## 1
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40002 | ID |  |  | 1
40003 | L |  |  | 66
40004 | Manufacturer (Mn) |  |  | Continental Control Systems | R
40020 | Model (Md) |  |  | WND-WR-MB | R
40036 | Options (Opt) |  |  | unimplemented | R
40044 | Version (Vr) |  |  | supported | R
40052 | Serial Number (SN) |  |  | supported | R
40068 | Device Address (DA) |  |  | supported | RW
40069 | Pad |  |  |  | R

## 203
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40070 | ID |  |  | 203
40071 | L |  |  | 105
40072 | Amps (A) |  |  | supported | R
40073 | Amps PhaseA (AphA) |  |  | supported | R
40074 | Amps PhaseB (AphB) |  |  | supported | R
40075 | Amps PhaseC (AphC) |  |  | supported | R
40076 | A_SF |  |  | supported | R
40077 | Voltage LN (PhV) |  |  | supported | R
40078 | Phase Voltage AN (PhVphA) |  |  | supported | R
40079 | Phase Voltage BN (PhVphB) |  |  | supported | R
40080 | Phase Voltage CN (PhVphC) |  |  | supported | R
40081 | Voltage LL (PPV) |  |  | supported | R
40082 | PhVphAB |  |  | supported | R
40083 | PhVphBC |  |  | supported | R
40084 | PhVphCA |  |  | supported | R
40085 | V_SF |  |  | supported | R
40086 | Hz |  |  | supported | R
40087 | Hz_SF |  |  | -2 | R
40088 | Watts (W) |  |  | supported | R
40089 | Watts phase A (WphA) |  |  | supported | R
40090 | Watts phase B (WphB) |  |  | supported | R
40091 | Watts phase C (WphC) |  |  | supported | R
40092 | W_SF |  |  | supported | R
40093 | VA |  |  | supported | R
40094 | VA phase A (VAphA) |  |  | supported | R
40095 | VA phase B (VAphB) |  |  | supported | R
40096 | VA phase C (VAphC) |  |  | supported | R
40097 | VA_SF |  |  | supported | R
40098 | VAR |  |  | supported | R
40099 | VAR phase A (VARphA) |  |  | supported | R
40100 | VAR phase B (VARphB) |  |  | supported | R
40101 | VAR phase C (VARphC) |  |  | supported | R
40102 | VAR_SF |  |  | supported | R
40103 | PF |  |  | supported | R
40104 | PF phase A (PFphA) |  |  | supported | R
40105 | PF phase B (PFphB) |  |  | supported | R
40106 | PF phase C (PFphC) |  |  | supported | R
40107 | PF_SF |  |  | -4 | R
40108 | Total Watt-hours Exported (TotWhExp) |  |  | supported | R
40110 | Total Watt-hours Exported phase A (TotWhExpPhA) |  |  | supported | R
40112 | Total Watt-hours Exported phase B (TotWhExpPhB) |  |  | supported | R
40114 | Total Watt-hours Exported phase C (TotWhExpPhC) |  |  | supported | R
40116 | Total Watt-hours Imported (TotWhImp) |  |  | supported | R
40118 | Total Watt-hours Imported phase A (TotWhImpPhA) |  |  | supported | R
40120 | Total Watt-hours Imported phase B (TotWhImpPhB) |  |  | supported | R
40122 | Total Watt-hours Imported phase C (TotWhImpPhC) |  |  | supported | R
40124 | TotWh_SF |  |  | 2 | R
40125 | Total VA-hours Exported (TotVAhExp) |  |  | unimplemented | R
40127 | Total VA-hours Exported phase A (TotVAhExpPhA) |  |  | unimplemented | R
40129 | Total VA-hours Exported phase B (TotVAhExpPhB) |  |  | unimplemented | R
40131 | Total VA-hours Exported phase C (TotVAhExpPhC) |  |  | unimplemented | R
40133 | Total VA-hours Imported (TotVAhImp) |  |  | supported | R
40135 | Total VA-hours Imported phase A (TotVAhImpPhA) |  |  | supported | R
40137 | Total VA-hours Imported phase B (TotVAhImpPhB) |  |  | supported | R
40139 | Total VA-hours Imported phase C (TotVAhImpPhC) |  |  | supported | R
40141 | TotVAh_SF |  |  | 2 | R
40142 | Total VAR-hours Imported Q1 (TotVArhImpQ1) |  |  | supported | R
40144 | Total VAr-hours Imported Q1 phase A (TotVArhImpQ1PhA) |  |  | supported | R
40146 | Total VAr-hours Imported Q1 phase B (TotVArhImpQ1PhB) |  |  | supported | R
40148 | Total VAr-hourse Imported Q1 phase C (TotVArhImpQ1PhC) |  |  | supported | R
40150 | Total VAr-hours Imported Q2 (TotVArhImpQ2) |  |  | unimplemented | R
40152 | Total VAr-hours Imported Q2 phase A (TotVArhImpQ2PhA) |  |  | unimplemented | R
40154 | Total VAr-hours Imported Q2 phase B (TotVArhImpQ2PhB) |  |  | unimplemented | R
40156 | Total VAr-hours Imported Q2 phase C (TotVArhImpQ2PhC) |  |  | unimplemented | R
40158 | Total VAr-hours Exported Q3 (TotVArhExpQ3) |  |  | supported | R
40160 | Total VAr-hours Exported Q3 phase A (TotVArhExpQ3PhA) |  |  | supported | R
40162 | Total VAr-hours Exported Q3 phase B (TotVArhExpQ3PhB) |  |  | supported | R
40164 | Total VAr-hours Exported Q3 phase C (TotVArhExpQ3PhC) |  |  | supported | R
40166 | Total VAr-hours Exported Q4 (TotVArhExpQ4) |  |  | unimplemented | R
40168 | Total VAr-hours Exported Q4 Imported phase A (TotVArhExpQ4PhA) |  |  | unimplemented | R
40170 | TotVArhExpQ4PhB |  |  | unimplemented | R
40172 | Total VAr-hours Exported Q4 Imported phase C (TotVArhExpQ4PhC) |  |  | unimplemented | R
40174 | TotVArh_SF |  |  | 2 | R
40175 | Events (Evt) |  |  | supported | R
|  | 2 | M_EVENT_Power_Failure | unimplemented
|  | 3 | M_EVENT_Under_Voltage | unimplemented
|  | 4 | M_EVENT_Low_PF | unimplemented
|  | 5 | M_EVENT_Over_Current | unimplemented
|  | 6 | M_EVENT_Over_Voltage | supported
|  | 7 | M_EVENT_Missing_Sensor | supported
|  | 8 | M_EVENT_Reserved1 | unimplemented
|  | 9 | M_EVENT_Reserved2 | unimplemented
|  | 10 | M_EVENT_Reserved3 | unimplemented
|  | 11 | M_EVENT_Reserved4 | unimplemented
|  | 12 | M_EVENT_Reserved5 | unimplemented
|  | 13 | M_EVENT_Reserved6 | unimplemented
|  | 14 | M_EVENT_Reserved7 | unimplemented
|  | 15 | M_EVENT_Reserved8 | unimplemented
|  | 16 | M_EVENT_OEM01 | unimplemented
|  | 17 | M_EVENT_OEM02 | unimplemented
|  | 18 | M_EVENT_OEM03 | unimplemented
|  | 19 | M_EVENT_OEM04 | unimplemented
|  | 20 | M_EVENT_OEM05 | unimplemented
|  | 21 | M_EVENT_OEM06 | unimplemented
|  | 22 | M_EVENT_OEM07 | unimplemented
|  | 23 | M_EVENT_OEM08 | unimplemented
|  | 24 | M_EVENT_OEM09 | unimplemented
|  | 25 | M_EVENT_OEM10 | unimplemented
|  | 26 | M_EVENT_OEM11 | unimplemented
|  | 27 | M_EVENT_OEM12 | unimplemented
|  | 28 | M_EVENT_OEM13 | unimplemented
|  | 29 | M_EVENT_OEM14 | unimplemented
|  | 30 | M_EVENT_OEM15 | unimplemented
|  |  | Power Failure (None) | unimplemented
|  |  | Under Voltage (None) | unimplemented
|  |  | Low PF (None) | unimplemented
|  |  | Over Current (None) | unimplemented
|  |  | Over Voltage (None) | supported
|  |  | Missing Sensor (None) | supported
|  |  | OEM01 (None) | unimplemented
|  |  | OEM02 (None) | unimplemented
|  |  | OEM01 (None) | unimplemented
|  |  | OEM04 (None) | unimplemented
|  |  | OEM05 (None) | unimplemented
|  |  | OEM06 (None) | unimplemented
|  |  | OEM07 (None) | unimplemented
|  |  | OEM08 (None) | unimplemented
|  |  | OEM09 (None) | unimplemented
|  |  | OEM10 (None) | unimplemented
|  |  | OEM11 (None) | unimplemented
|  |  | OEM12 (None) | unimplemented
|  |  | OEM13 (None) | unimplemented
|  |  | OEM14 (None) | unimplemented
|  |  | OEM15 (None) | unimplemented
|  |  | OEM16 (None) | unimplemented

## 213
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40177 | ID |  |  | 213
40178 | L |  |  | 124
40179 | Amps (A) |  |  | supported | R
40181 | Amps PhaseA (AphA) |  |  | supported | R
40183 | Amps PhaseB (AphB) |  |  | supported | R
40185 | Amps PhaseC (AphC) |  |  | supported | R
40187 | Voltage LN (PhV) |  |  | supported | R
40189 | Phase Voltage AN (PhVphA) |  |  | supported | R
40191 | Phase Voltage BN (PhVphB) |  |  | supported | R
40193 | Phase Voltage CN (PhVphC) |  |  | supported | R
40195 | Voltage LL (PPV) |  |  | supported | R
40197 | Phase Voltage AB (PPVphAB) |  |  | supported | R
40199 | Phase Voltage BC (PPVphBC) |  |  | supported | R
40201 | Phase Voltage CA (PPVphCA) |  |  | supported | R
40203 | Hz |  |  | supported | R
40205 | Watts (W) |  |  | supported | R
40207 | Watts phase A (WphA) |  |  | supported | R
40209 | Watts phase B (WphB) |  |  | supported | R
40211 | Watts phase C (WphC) |  |  | supported | R
40213 | VA |  |  | supported | R
40215 | VA phase A (VAphA) |  |  | supported | R
40217 | VA phase B (VAphB) |  |  | supported | R
40219 | VA phase C (VAphC) |  |  | supported | R
40221 | VAR |  |  | supported | R
40223 | VAR phase A (VARphA) |  |  | supported | R
40225 | VAR phase B (VARphB) |  |  | supported | R
40227 | VAR phase C (VARphC) |  |  | supported | R
40229 | PF |  |  | supported | R
40231 | PF phase A (PFphA) |  |  | supported | R
40233 | PF phase B (PFphB) |  |  | supported | R
40235 | PF phase C (PFphC) |  |  | supported | R
40237 | Total Watt-hours Exported (TotWhExp) |  |  | supported | R
40239 | Total Watt-hours Exported phase A (TotWhExpPhA) |  |  | supported | R
40241 | Total Watt-hours Exported phase B (TotWhExpPhB) |  |  | supported | R
40243 | Total Watt-hours Exported phase C (TotWhExpPhC) |  |  | supported | R
40245 | Total Watt-hours Imported (TotWhImp) |  |  | supported | R
40247 | Total Watt-hours Imported phase A (TotWhImpPhA) |  |  | supported | R
40249 | Total Watt-hours Imported phase B (TotWhImpPhB) |  |  | supported | R
40251 | Total Watt-hours Imported phase C (TotWhImpPhC) |  |  | supported | R
40253 | Total VA-hours Exported (TotVAhExp) |  |  | unimplemented | R
40255 | Total VA-hours Exported phase A (TotVAhExpPhA) |  |  | unimplemented | R
40257 | Total VA-hours Exported phase B (TotVAhExpPhB) |  |  | unimplemented | R
40259 | Total VA-hours Exported phase C (TotVAhExpPhC) |  |  | unimplemented | R
40261 | Total VA-hours Imported (TotVAhImp) |  |  | supported | R
40263 | Total VA-hours Imported phase A (TotVAhImpPhA) |  |  | supported | R
40265 | Total VA-hours Imported phase B (TotVAhImpPhB) |  |  | supported | R
40267 | Total VA-hours Imported phase C (TotVAhImpPhC) |  |  | supported | R
40269 | Total VAR-hours Imported Q1 (TotVArhImpQ1) |  |  | supported | R
40271 | TotVArhImpQ1phA |  |  | supported | R
40273 | TotVArhImpQ1phB |  |  | supported | R
40275 | TotVArhImpQ1phC |  |  | supported | R
40277 | Total VAr-hours Imported Q2 (TotVArhImpQ2) |  |  | unimplemented | R
40279 | TotVArhImpQ2phA |  |  | unimplemented | R
40281 | TotVArhImpQ2phB |  |  | unimplemented | R
40283 | TotVArhImpQ2phC |  |  | unimplemented | R
40285 | Total VAr-hours Exported Q3 (TotVArhExpQ3) |  |  | supported | R
40287 | TotVArhExpQ3phA |  |  | supported | R
40289 | TotVArhExpQ3phB |  |  | supported | R
40291 | TotVArhExpQ3phC |  |  | supported | R
40293 | Total VAr-hours Exported Q4 (TotVArhExpQ4) |  |  | unimplemented | R
40295 | TotVArhExpQ4phA |  |  | unimplemented | R
40297 | TotVArhExpQ4phB |  |  | unimplemented | R
40299 | TotVArhExpQ4phC |  |  | unimplemented | R
40301 | Events (Evt) |  |  | supported | R
|  | 2 | M_EVENT_Power_Failure | unimplemented
|  | 3 | M_EVENT_Under_Voltage | unimplemented
|  | 4 | M_EVENT_Low_PF | unimplemented
|  | 5 | M_EVENT_Over_Current | unimplemented
|  | 6 | M_EVENT_Over_Voltage | supported
|  | 7 | M_EVENT_Missing_Sensor | supported
|  | 8 | M_EVENT_Reserved1 | unimplemented
|  | 9 | M_EVENT_Reserved2 | unimplemented
|  | 10 | M_EVENT_Reserved3 | unimplemented
|  | 11 | M_EVENT_Reserved4 | unimplemented
|  | 12 | M_EVENT_Reserved5 | unimplemented
|  | 13 | M_EVENT_Reserved6 | unimplemented
|  | 14 | M_EVENT_Reserved7 | unimplemented
|  | 15 | M_EVENT_Reserved8 | unimplemented
|  | 16 | M_EVENT_OEM01 | unimplemented
|  | 17 | M_EVENT_OEM02 | unimplemented
|  | 18 | M_EVENT_OEM03 | unimplemented
|  | 19 | M_EVENT_OEM04 | unimplemented
|  | 20 | M_EVENT_OEM05 | unimplemented
|  | 21 | M_EVENT_OEM06 | unimplemented
|  | 22 | M_EVENT_OEM07 | unimplemented
|  | 23 | M_EVENT_OEM08 | unimplemented
|  | 24 | M_EVENT_OEM09 | unimplemented
|  | 25 | M_EVENT_OEM10 | unimplemented
|  | 26 | M_EVENT_OEM11 | unimplemented
|  | 27 | M_EVENT_OEM12 | unimplemented
|  | 28 | M_EVENT_OEM13 | unimplemented
|  | 29 | M_EVENT_OEM14 | unimplemented
|  | 30 | M_EVENT_OEM15 | unimplemented
|  |  | Power Failure (None) | unimplemented
|  |  | Under Voltage (None) | unimplemented
|  |  | Low PF (None) | unimplemented
|  |  | Over Current (None) | unimplemented
|  |  | Over Voltage (None) | supported
|  |  | Missing Sensor (None) | supported
|  |  | OEM01 (None) | unimplemented
|  |  | OEM02 (None) | unimplemented
|  |  | OEM01 (None) | unimplemented
|  |  | OEM04 (None) | unimplemented
|  |  | OEM05 (None) | unimplemented
|  |  | OEM06 (None) | unimplemented
|  |  | OEM07 (None) | unimplemented
|  |  | OEM08 (None) | unimplemented
|  |  | OEM09 (None) | unimplemented
|  |  | OEM10 (None) | unimplemented
|  |  | OEM11 (None) | unimplemented
|  |  | OEM12 (None) | unimplemented
|  |  | OEM13 (None) | unimplemented
|  |  | OEM14 (None) | unimplemented
|  |  | OEM15 (None) | unimplemented
|  |  | OEM16 (None) | unimplemented

## 64080
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40303 | ID |  |  | 64080
40304 | L |  |  | 29
40305 | CT1 Amps rating (CtAmps1) |  |  | supported | RW | Corresponds to AphA. Write limits: 0 to 30000
40306 | CT2 Amps rating (CtAmps2) |  |  | supported | RW | Corresponds to AphB. Write limits: 0 to 30000
40307 | CT3 Amps rating (CtAmps3) |  |  | supported | RW | Corresponds to AphC. Write limits: 0 to 30000
40308 | Bitmap for reversing CT directions (CtDirections) |  |  | supported | RW | Write limits: 0 to 7
|  | 0 | REVERSE_CT1 |  |  | Resetting bit 0 selects normal direction; setting it reverses the direction
|  | 1 | REVERSE_CT2 |  |  | Resetting bit 1 selects normal direction; setting it reverses the direction
|  | 2 | REVERSE_CT3 |  |  | Resetting bit 2 selects normal direction; setting it reverses the direction
40309 | Potential transformer ratio (PtRatio) |  |  | supported | RW | Write limits: 0.5 to 300.0
40311 | Amount of averaging applied to readings (Averaging) |  |  | supported | RW | Write limits: 0 to 3 and 100 to 60000 (0, 1, 2 or 3 selects interval of 0.1, 5, 20 or 60 seconds respectively; 100 to 60000 selects any interval in milliseconds)
40312 | Mains connection type (ConnectionType) |  |  | supported | RW | Write limits: 0 to 5 (0=Custom, 1=Wye, 2=Delta, 3=Branch circuits, 4=House and inverter, 5=Line to Line)
40313 | Voltage paired with CT1 (MeterConfig1) |  |  | supported | RW | Write limits: 0, 10, 20, 30, 40, 50, 60, 70, 80 or 90 (0=Disable meter element, 10=Va, 20=Vb, 30=Vc, 40=Vab, 50=Vbc, 60=Vca, 70=Vba, 80=Vcb, 90=Vac)
40314 | Voltage paired with CT2 (MeterConfig2) |  |  | supported | RW | Write limits: 0, 10, 20, 30, 40, 50, 60, 70, 80 or 90 (0=Disable meter element, 10=Va, 20=Vb, 30=Vc, 40=Vab, 50=Vbc, 60=Vca, 70=Vba, 80=Vcb, 90=Vac)
40315 | Voltage paired with CT3 (MeterConfig3) |  |  | supported | RW | Write limits: 0, 10, 20, 30, 40, 50, 60, 70, 80 or 90 (0=Disable meter element, 10=Va, 20=Vb, 30=Vc, 40=Vab, 50=Vbc, 60=Vca, 70=Vba, 80=Vcb, 90=Vac)
40316 | Enable monitoring for disconnected CTs (CtMonitoring) |  |  | supported | RW | Write limits: 0 to 2 (0, 1 or 2 selects no CT detect, CT detect enabled or CT detect enabled/latching, respectively)
40317 | CT1 connected status (CtStatus1) |  |  | supported | RW | Corresponds to AphA. Write limits: 0 only (resets CtStatus1)
40318 | CT2 connected status (CtStatus2) |  |  | supported | RW | Corresponds to AphB. Write limits: 0 only (resets CtStatus2)
40319 | CT3 connected status (CtStatus3) |  |  | supported | RW | Corresponds to AphC. Write limits: 0 only (resets CtStatus3)
40320 | CT1 fullscale signal voltage (NominalCtVolts1) |  |  | supported | RW | Write limits: 0.1 to 1.25
40322 | CT2 fullscale signal voltage (NominalCtVolts2) |  |  | supported | RW | Write limits: 0.1 to 1.25
40324 | CT3 fullscale signal voltage (NominalCtVolts3) |  |  | supported | RW | Write limits: 0.1 to 1.25
40326 | Newest error or status code (ErrorStatus1) |  |  | supported | RW | Write limits: 0 only (resets all 8 ErrorStatus registers)
40327 | Error or status code (ErrorStatus2) |  |  | supported | RW | Write limits: 0 only (resets all 8 ErrorStatus registers)
40328 | Error or status code (ErrorStatus3) |  |  | supported | RW | Write limits: 0 only (resets all 8 ErrorStatus registers)
40329 | Error or status code (ErrorStatus4) |  |  | supported | RW | Write limits: 0 only (resets all 8 ErrorStatus registers)
40330 | Error or status code (ErrorStatus5) |  |  | supported | RW | Write limits: 0 only (resets all 8 ErrorStatus registers)
40331 | Error or status code (ErrorStatus6) |  |  | supported | RW | Write limits: 0 only (resets all 8 ErrorStatus registers)
40332 | Error or status code (ErrorStatus7) |  |  | supported | RW | Write limits: 0 only (resets all 8 ErrorStatus registers)
40333 | Oldest error or status code (ErrorStatus8) |  |  | supported | RW | Write limits: 0 only (resets all 8 ErrorStatus registers)