WattNodePlus Electric Power Meter

With LonWorks® Free-Topology Transceiver

Engineering Specifications

- The power meter shall make true RMS power measurements on multi-phase electrical circuits.

- The power meter shall transmit the following readings:

  - Real power (watts) total for all phases and for each phase

  - Real energy (watt-hours) consumed total for all phases and for each phase

  - Demand (watts) over user specified interval (block or sliding window)

  - Peak demand (watts) and time of peak demand since reset

  - Current (amps) for each phase

  - Phase-to-neutral or phase-to-ground (delta models) voltage

  - Power factor for each phase and average

  - Reactive power (watts) total for all phases and for each phase

  - AC frequency

- The power meter shall communicate using the LonTalk® protocol (ANSI/CEA-709.1-B-2002) and LonMark specified TP/FT-10 free-topology and bus twisted-pair transceiver (ANSI/CEA-709.3).

- The power meter shall have a unique Neuron ID number which is externally visible.

- The power meter shall be UL and cUL listed and meet safety standards UL1244 or UL 61010-1.

- The power meter shall derive operating power from its metering connections, and shall not require a separate power connection.

- Power meter models must be available to directly accept voltage input at one of the following voltages: 120, 208-240, 277, 347 or 480 VAC (50 or 60Hz).

- The power meter shall accept 0 to 0.333VAC input from up to three current transducers.

- The power meter shall be fitted with detachable terminal blocks for all wiring connections.

- The measured energy consumption shall be retained in non-volatile memory.

- The demand measurement shall be programmable for intervals of 5 to 720 minutes with up to 8 subintervals.

- The maximum demand and time of maximum demand shall be stored in non-volatile memory and can be reset.

- The power meter shall log at least 35 days of total real energy readings at 15 minute intervals to non-volatile memory.

- The power meter shall be calibrated with NIST traceable standards to an accuracy of 0.5% or better.

- The power meter shall operate from -30C to +60C.

- The power meter shall have dimensions not exceeding 5.7” x 3.4” x 1.5”.

- The power meter shall be Continental Control Systems’ WattNode Plus model.